12 GeV Hall D Complex – Concept Design Update
1 Mar 06

Page 2 of 4

	Design Analysis Section / Page No.
	Cmt

#
	Reviewer
	JLAB Review Comment
	A/E Response

	44
	1
	R. Jones
	Is the quadrupole magnet and PS missing?
	

	47
	2
	R. Jones
	Are both collimator magnets and PS included or only one?  There are two identical magnets in the design.
	

	47
	3
	R. Jones
	Appendix (Summary of Conference) p.10/23 item 1. (Collimator) part b says “LCW needed for a magnet(s)” but table on p.47 shows only HVAC load for collimator magnet PS (see also cmt 2 above)
	

	Dwg 6/16
	4
	R. Jones
	Elevation of tagger area relative to beam height is wrong (cf. dwg 12/16).  Beam should be nearer to floor (1.8m) than it is to the ceiling (2.5 m)
	

	Dwg 6/16
	5
	R. Jones
	10” beam pipe (heavy line) appears to begin about 5m downstream of the beam exit from the tagger area.  It should begin inside the tagger area, downstream of the permanent magnet (dwg. 10/16).
	

	Dwg 12/16
	6
	R. Jones
	“Section through electron beam dump” should not intersect any interior region of the tagger area, only the electron beam dump (see location of section on dwg 6/12)
	

	Dwg 10/16
	7
	R. Jones
	Cross-sectional area of electron beam dump tunnel should be minimized, consistent with access requirements, because that tunnel area upstream of the dump itself must be filled with shielding materials prior to tagged beam operation.
	

	Dwg 10/16
	8
	R. Jones
	Electron beam dump must be moved to the downstream end of the tunnel and the upstream region filled with stacked shielding except for a hole for the electron beam vacuum tube.
	

	Dwg 7/16
	9
	R. Jones
	One or two penetrations through the exterior wall of the Hall D experimental area are requested by survey crew to enable line-of-sight to alignment fixtures inside the Hall from exterior locations on the site.
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	


	Concept Dwg No
	Cmt

#
	Reviewer
	JLAB Review Comment
	A/E Response

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	


	Cost Estimate Section / Page
	Cmt

#
	Reviewer
	JLAB Review Comment
	A/E Response

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	


